## Tabelle1
1.Real-time data 0x0000～0x03F Including: switch port, electric relay, dial switch, fault and other data
Address | Parameter Name | Range | Default | Type | Note | Bit Label
0x0000 | Running Status 1 | Standard Bits |  | Read-Only | 1: Function ON 0: Function OFF | Bit0 Refrigerator recycling Bit1 First level anti-freezing Bit2 Second level anti-freezing Bit3 failure warning Bit4 System 1 return oil Bit5 Bit6 Bit7 Bit8 System defrost Bit9 Bit10 Bit11 Bit12 Constant temperature shutdown Bit13 Fault shutdown protection Bit14 Machine run Bit15 Machine wait to run
0x0001 | Running Status 2 | Standard Bits |  | Read-Only | 1: Function ON 0: Function OFF | Bit0 High temperature Sterilization Bit1 "High temperature Sterilization Heat Preservation" Bit2 Bit3 Bit4 Bit5 Bit6 Bit7 Bit8 Bit9 Bit10 Controller on / off Bit11 Bit12 Bit13 Bit14 Bit15
0x0002 | Fault State 1 | Standard Bits |  | Read-Only |  | Bit0 Wrong phase fault Bit1 Lack of phase fault Bit2 Water flow fault Bit3 Communication fault Bit4 Emergency fault Bit5 Use time expired Bit6 Water tank (down) temperature fault Bit7 Water inlet temperature fault Bit8 Indoor temperature fault Bit9 Environmental temperature fault Bit10 User backwater temperature fault Bit11 Cooling outlet water level is too low Bit12 Water level switch fault Bit13 Water outlet temperature fault Bit14 heating outlet water level is too high Bit15 Protection against excessive water temperature difference between inlet and outlet
0x0003 | Fault State 2 | Standard Bits |  | Read-Only |  | Bit0 "Environmental low temperature protection" Bit1 Bit2 Bit3 Bit4 Bit5 Bit6 "Indoor environment humidity fault" Bit7 Bit8 Bit9 Bit10 Bit11 Phase order dial error Bit12 Bit13 "Water pump 1 feedback fault" Bit14 Water pump 2 feedback fault Bit15 Low water flow protection
0x0004 | Fault State 3 | Standard Bits |  | Read-Only |  | Bit0 "Phase sequence disconnected" Bit1 Expansion board communication Bit2 "Plate Heat Exchanger temperature fault" Bit3 "Fan motor 1 communication fault" Bit4 Fan motor 2 communication fault Bit5 "Online model not matching error" Bit6 "Auxiliary Heating Source Hot Water Sensor Error" Bit7 Auxiliary Heating Source Heating Sensor Error Bit8 Buffer Tank Error Bit9 "Main Water Outlet Temperature Error" Bit10 Reserved Bit11 Reserved Bit12 Reserved Bit13 Reserved Bit14 Reserved Bit15 Reserved
0x0005 | System 1 Fault State 1 | Standard Bits |  | Read-Only |  | Bit0: high pressure switch protection Bit1: Low pressure switch protection Bit2: High pressure over high protection Bit3: Low pressure over low protection Bit4: Exhaust over protection Bit5: Current protection Bit6: Coil Temperature over protection Bit7: Coil temperature fault Bit8: Return air temperature fault Bit9: Exhaust temperature fault Bit10: Economizer Inlet temperature fault Bit11: Economizer Outlet temperature fault Bit12: Fan drive communication fault Bit13: DC fan fault Bit14: Refrigeration coil temperature fault Bit15: Reserved
0x0006 | System 1 Fault State 2 | Standard Bits |  | Read-Only |  | Bit0: High pressure sensor fault Bit1: Low pressure sensor fault Bit2: Middle Pressure switch fault Bit3: Coil Temperature over high Bit4: Compressor Drive Board communication fault Bit5: Bit6: Bit7: Bit8: Bit9: Bit10: Bit11: Bit12: Bit13: Bit14: Bit15:
0x0007 | System 1 Drive Fault State 1 | Standard Bits |  | Read-Only |  | Bit0: IPM overcurrent/IPM module protection Bit1: Compressor drive fault Bit2: compressor overcurrent Bit3: Input voltage phase loss Bit4: IPM current sampling fault Bit5: Overheating shutdown of power components Bit6: Precharge failed Bit7: DC bus overvoltage Bit8: DC bus undervoltage Bit9: AC input undervoltage Bit10: AC input overcurrent Bit11: Input voltage sampling fault Bit12: DSP and PFC communication fault Bit13: Radiator temperature sensor fault Bit14: Communication failure between DSP and communication board Bit15: Abnormal communication with the main control board
0x0008 | System 1 Drive Fault State 2 | Standard Bits |  | Read-Only |  | Bit0: Compressor overcurrent alarm Bit1: "Compressor field weakening protection alarm Bit2: PIM overheat alarm Bit3: PFC overheat alarm Bit4: AC input overcurrent alarm Bit5: EEPROM fault alarm Bit6: NA Bit7: EEPROM refresh completed Bit8: Temperature sensing fault frequency limit; Bit9: AC undervoltage and frequency limit protection alarm Bit10: NA Bit11: NA Bit12: NA Bit13: NA Bit14: NA Bit15: NA
0x0009 | System 1 Drive Fault State 3 | Standard Bits |  | Read-Only |  | Bit0: IPM module thermal shutdown Bit1: Compressor phase loss Bit2: compressor overload Bit3: Input current sampling fault Bit4: PIM supply voltage fault Bit5: Precharge circuit voltage fault Bit6: EEPROM fault Bit7: AC input overvoltage fault Bit8: Microelectronics fault Bit9: Compressor model code fault Bit10: Current sampling signal overcurrent Bit11: NA Bit12: NA Bit13: NA Bit14: NA Bit15: NA
0x000A | System 2 Fault State 1 | Standard Bits |  | Read-Only |  | Bit0: high pressure switch protection Bit1: Low pressure switch protection Bit2: High pressure over high protection Bit3: Low pressure over low protection Bit4: Exhaust over protection Bit5: Current protection Bit6: Coil Temperature over protection Bit7: Coil temperature fault Bit8: Return air temperature fault Bit9: Exhaust temperature fault Bit10: Economizer Inlet temperature fault Bit11: Economizer Outlet temperature fault Bit12: Fan drive communication fault Bit13: DC fan fault Bit14: Refrigeration coil temperature fault Bit15: Reserved
0x000B | System 2 Fault State 2 | Standard Bits |  | Read-Only |  | Bit0: High pressure sensor fault Bit1: Low pressure sensor fault Bit2: Middle Pressure switch fault Bit3: Coil Temperature over high Bit4: Compressor Drive Board communication fault Bit5: Bit6: Bit7: Bit8: Bit9: Bit10: Bit11: Bit12: Bit13: Bit14: Bit15:
0x000C | System 2 Drive Fault State 1 | Standard Bits |  | Read-Only |  | Bit0: IPM overcurrent/IPM module protection Bit1: Compressor drive fault Bit2: compressor overcurrent Bit3: Input voltage phase loss Bit4: IPM current sampling fault Bit5: Overheating shutdown of power components Bit6: Precharge failed Bit7: DC bus overvoltage Bit8: DC bus undervoltage Bit9: AC input undervoltage Bit10: AC input overcurrent Bit11: Input voltage sampling fault Bit12: DSP and PFC communication fault Bit13: Radiator temperature sensor fault Bit14: Communication failure between DSP and communication board Bit15: Abnormal communication with the main control board
0x000D | System 2 Drive Fault State 2 | Standard Bits |  | Read-Only |  | Bit0: Compressor overcurrent alarm Bit1: "Compressor field weakening protection alarm Bit2: PIM overheat alarm Bit3: PFC overheat alarm Bit4: AC input overcurrent alarm Bit5: EEPROM fault alarm Bit6: NA Bit7: EEPROM refresh completed Bit8: Temperature sensing fault frequency limit; Bit9: AC undervoltage and frequency limit protection alarm Bit10: NA Bit11: NA Bit12: NA Bit13: NA Bit14: NA Bit15: NA
0x000E | System 2 Drive Fault State 3 | Standard Bits |  | Read-Only |  | Bit0: IPM module thermal shutdown Bit1: Compressor phase loss Bit2: compressor overload Bit3: Input current sampling fault Bit4: PIM supply voltage fault Bit5: Precharge circuit voltage fault Bit6: EEPROM fault Bit7: AC input overvoltage fault Bit8: Microelectronics fault Bit9: Compressor model code fault Bit10: Current sampling signal overcurrent Bit11: NA Bit12: NA Bit13: NA Bit14: NA Bit15: NA
0x000F | System 3 Fault State 1 | Standard Bits |  | Read-Only |  | Bit0: high pressure switch protection Bit1: Low pressure switch protection Bit2: High pressure over high protection Bit3: Low pressure over low protection Bit4: Exhaust over protection Bit5: Current protection Bit6: Coil Temperature over protection Bit7: Coil temperature fault Bit8: Return air temperature fault Bit9: Exhaust temperature fault Bit10: Economizer Inlet temperature fault Bit11: Economizer Outlet temperature fault Bit12: Fan drive communication fault Bit13: DC fan fault Bit14: Refrigeration coil temperature fault Bit15: Reserved
0x0010 | System 3 Fault State 2 | Standard Bits |  | Read-Only |  | Bit0: High pressure sensor fault Bit1: Low pressure sensor fault Bit2: Middle Pressure switch fault Bit3: Coil Temperature over high Bit4: Compressor Drive Board communication fault Bit5: Bit6: Bit7: Bit8: Bit9: Bit10: Bit11: Bit12: Bit13: Bit14: Bit15:
0x0011 | System 3 Drive Fault State 1 | Standard Bits |  | Read-Only |  | Bit0: IPM overcurrent/IPM module protection Bit1: Compressor drive fault Bit2: compressor overcurrent Bit3: Input voltage phase loss Bit4: IPM current sampling fault Bit5: Overheating shutdown of power components Bit6: Precharge failed Bit7: DC bus overvoltage Bit8: DC bus undervoltage Bit9: AC input undervoltage Bit10: AC input overcurrent Bit11: Input voltage sampling fault Bit12: DSP and PFC communication fault Bit13: Radiator temperature sensor fault Bit14: Communication failure between DSP and communication board Bit15: Abnormal communication with the main control board
0x0012 | System 3 Drive Fault State 2 | Standard Bits |  | Read-Only |  | Bit0: Compressor overcurrent alarm Bit1: "Compressor field weakening protection alarm Bit2: PIM overheat alarm Bit3: PFC overheat alarm Bit4: AC input overcurrent alarm Bit5: EEPROM fault alarm Bit6: NA Bit7: EEPROM refresh completed Bit8: Temperature sensing fault frequency limit; Bit9: AC undervoltage and frequency limit protection alarm Bit10: NA Bit11: NA Bit12: NA Bit13: NA Bit14: NA Bit15: NA
0x0013 | System 3 Drive Fault State 3 | Standard Bits |  | Read-Only |  | Bit0: IPM module thermal shutdown Bit1: Compressor phase loss Bit2: compressor overload Bit3: Input current sampling fault Bit4: PIM supply voltage fault Bit5: Precharge circuit voltage fault Bit6: EEPROM fault Bit7: AC input overvoltage fault Bit8: Microelectronics fault Bit9: Compressor model code fault Bit10: Current sampling signal overcurrent Bit11: NA Bit12: NA Bit13: NA Bit14: NA Bit15: NA
0x0014 | System 4 Fault State 1 | Standard Bits |  | Read-Only |  | Bit0: high pressure switch protection Bit1: Low pressure switch protection Bit2: High pressure over high protection Bit3: Low pressure over low protection Bit4: Exhaust over protection Bit5: Current protection Bit6: Coil Temperature over protection Bit7: Coil temperature fault Bit8: Return air temperature fault Bit9: Exhaust temperature fault Bit10: Economizer Inlet temperature fault Bit11: Economizer Outlet temperature fault Bit12: Fan drive communication fault Bit13: DC fan fault Bit14: Refrigeration coil temperature fault Bit15: Reserved
0x0015 | System 4 Fault State 2 | Standard Bits |  | Read-Only |  | Bit0: High pressure sensor fault Bit1: Low pressure sensor fault Bit2: Middle Pressure switch fault Bit3: Coil Temperature over high Bit4: Compressor Drive Board communication fault Bit5: Bit6: Bit7: Bit8: Bit9: Bit10: Bit11: Bit12: Bit13: Bit14: Bit15:
0x0016 | System 4 Drive Fault State 1 | Standard Bits |  | Read-Only |  | Bit0: IPM overcurrent/IPM module protection Bit1: Compressor drive fault Bit2: compressor overcurrent Bit3: Input voltage phase loss Bit4: IPM current sampling fault Bit5: Overheating shutdown of power components Bit6: Precharge failed Bit7: DC bus overvoltage Bit8: DC bus undervoltage Bit9: AC input undervoltage Bit10: AC input overcurrent Bit11: Input voltage sampling fault Bit12: DSP and PFC communication fault Bit13: Radiator temperature sensor fault Bit14: Communication failure between DSP and communication board Bit15: Abnormal communication with the main control board
0x0017 | System 4 Drive Fault State 2 | Standard Bits |  | Read-Only |  | Bit0: Compressor overcurrent alarm Bit1: "Compressor field weakening protection alarm Bit2: PIM overheat alarm Bit3: PFC overheat alarm Bit4: AC input overcurrent alarm Bit5: EEPROM fault alarm Bit6: NA Bit7: EEPROM refresh completed Bit8: Temperature sensing fault frequency limit; Bit9: AC undervoltage and frequency limit protection alarm Bit10: NA Bit11: NA Bit12: NA Bit13: NA Bit14: NA Bit15: NA
0x0018 | System 4 Drive Fault State 3 | Standard Bits |  | Read-Only |  | Bit0: IPM module thermal shutdown Bit1: Compressor phase loss Bit2: compressor overload Bit3: Input current sampling fault Bit4: PIM supply voltage fault Bit5: Precharge circuit voltage fault Bit6: EEPROM fault Bit7: AC input overvoltage fault Bit8: Microelectronics fault Bit9: Compressor model code fault Bit10: Current sampling signal overcurrent Bit11: NA Bit12: NA Bit13: NA Bit14: NA Bit15: NA
0x0019 | Relay output status 1 | Standard Bits |  | Read-Only |  | Bit0: Hot water electric heating Bit1: Fan high wind Bit2: Bit3: Fan low wind Bit4: Air conditioner electric heating Bit5: floor heating electric heating Bit6: Main engine circulating water pump Bit7: Bit8: Bit9: Electric crankshaft heating Bit10: Chassis electric heating Bit11: Return valve/pump Bit12: Bit13: Bit14: Air conditioner solenoid valve/three-way valve Bit15: Floor heating solenoid valve / three-way valve
0x001A | Relay output status 2 | Standard Bits |  | Read-Only |  | Bit0: Compressor 1 Bit1: Liquid injection solenoid valve 1 Bit2: Enthalpy solenoid valve 1 Bit3: Four-way valve 1 Bit4: Throttle bypass valve 1 Bit5: Fan motor 1 Bit6: Bit7: Bit8: Auxiliary Heating Pump Bit9: Bit10: Compressor 2 Bit11: Spray solenoid valve 2 Bit12: Enthalpy increasing solenoid valve 2 Bit13: 4-Way 2 Bit14: Bit15:
0x001B | Relay output status 3 | Standard Bits |  | Read-Only |  | Bit0: Bit1: Bit2: Bit3: Bit4: Bit5: Bit6: Expansion Tank Heating Element Bit7: Auxiliary Heat Source Hot water Pump Bit8: Auxiliary Heat Source Heating Pump Bit9: Gas Output Bit10: Bit11: Bit12: Bit13: Bit14: Bit15:
0x001C | Relay output status 4 | Standard Bits |  | Read-Only |  | Bit0: Pipeline electric heating 1 Bit1: Pipeline electric heating 2 Bit2: Bit3: Bit4: Bit5: Bit6: Bit7: Bit8: Bit9: Bit10: Bit11: Bit12: Bit13: Bit14: Bit15:
0x001D | Switch Port State 1 | Standard Bits |  | Read-Only |  | Bit0: SW1 Bit1: SW2 Bit2: SW3 Bit3: SW4 Bit4: SW5 Bit5: SW6 Bit6: SW7 Bit7: SW8 Bit8: Water Flow Switch Bit9: Bit10: House Heating Linkage Switch Bit11: Auxiliary Hot Water Linkage Switch Bit12: Linkage switch Bit13: emergency switch Bit14: Bit15:
0x001E | Switch Port State 2 | Standard Bits |  | Read-Only |  | Bit0: Bit1: Bit2: Bit3: Bit4: Bit5: Bit6: Bit7: High Pressure 1 Switch Bit8: Low Pressure 1 switch Bit9: Medium Pressure 1 switch Bit10: High Pressure 2 Switch Bit11: Low Pressure 2 switch Bit12: Medium Pressure 2 switch Bit13: Bit14: Bit15:
0x001F | Switch Port State 3 | Standard Bits |  | Read-Only |  | Bit0: Bit1: Bit2: Bit3: Bit4: Bit5: Auxiliary Heating Linkage Switch Bit6: Bit7: Bit8: Bit9: Bit10: Bit11: Bit12: Bit13: Bit14: Bit15:
0x0020 | Switch Port State 4 | Standard Bits |  | Read-Only |  | Bit0: Bit1: Bit2: Bit3: Bit4: Bit5: Bit6: Bit7: Bit8: Bit9: Bit10: Bit11: Bit12: Bit13: Bit14: Bit15:
0x0024 | Current unit tooling No | Actual Value |  | Read-Only
0x0027 | Compressor 1 Target frequency | Actual Value |  | Read-Only
0x0028 | Compressor 2 Target frequency | Actual Value |  | Read-Only